| POLICIES AND PROCEDURES | Approved |
| --- | --- |
| NAME OF FACILITY | Number: XXXXX |
| Department: All Departments | Page 1 of 3 |
| Subject: Maintaining Continuity of Smoke Barriers - Life Safety Code - K-25 Title: Above Ceiling Permit and Standards |
| Revision Dates: XX/XX/XXXX | Original Policy Date: XX/XX/XXXX |

### Purpose:

The process of above ceiling permitting/inspections to monitor and guide nursing facility staff, vendors, contractors and sub contractors in the process of proper closure of Non-rated and Rated Wall, floor, and ceiling penetrations. The intent is to maintain the facility in full compliances with CMS, NFPA, and applicable local and state Building Codes.

Policy:

All rated and non-rated fire and smoke barriers at FACILITY NAME shall be maintained in a condition equal to or better than original construction in terms of fire and smoke safety.  Installing contractors are responsible for the reporting of breaches of any fire or smoke barrier that they create or discover in the course of their operations to Plant Operations. The Plant Operations department will enforce this policy.

### Responsibility:

- The Plant Operations Department is responsible for monitoring and maintaining all systems above the ceilings. (Wiring, cabling, ducting, and piping).

- The Plant Operations Department is responsible for conducting all final inspection and closing out the ceilings with the contractor, sub contractor or vendor.

- All contractors, sub contractors and vendors who are required to conduct business above the ceiling are responsible for obtaining an above ceiling permit from the Plant Operations Department.

- All contractors, sub contractors and vendors and responsible for ensuring that there is a final inspection of their work prior to closing of any ceilings

- It is the contractor, sub contractors and vendors responsibility to request a pre above ceiling inspection to identify issues of concerns. If this inspection is not requested and completed, the contractor, sub contractor or vendor will take responsibility in bring all above ceiling penetrations along with any system they were installing, moving or modifying up to facility standards.

- All systems and penetrations must remain in compliance with the Life Safety Code.

### Procedure:

- All contractors, sub contractors and vendors will be properly identified by a badge and have an above ceiling permit.

- The above ceiling permit will be displayed in full view on the ladder(s) in the working area.

- All contractors, sub contractors and vendors will be indoctrinated in conducting above ceiling work with. The contractor, sub contractor or vendor will tour the area(s) where work will be accomplished.

- All ladders used in above ceiling work will not be made of any type of conductive material to protect the technician from electrical shock.

- All ladders will have the required OSHA and safety label on their ladders.

- Contractors will have all their ladders clearly mark for the ease of identification.  Plant Operations Department will do the same.

- During the periods of above ceiling work the craft or technician will ensure that no wires will be hanging down in a loop or loose that could cause injury to another person. If wire needs to hang down from the ceiling, they need to hang to the floor or above a height of 7 feet.

- During the periods of above ceiling work, if the ceiling is going to be abandoned for a period of more than 30 minutes the ceiling tiles will be re-installed.

- During the periods of meals and breaks, all ceilings will be closed for maximum fire protection.

- Any penetration through a non-rated or rated fire assembly will require proper fire stopping.  Contractor, sub contractor, or vendor must have the type of fire stopping material approved by Plant Operations. The type of fire stopping must be noted on the permit.

- The contractor shall review with Plant Operations department the following morning all penetrations completed the previous day prior to starting the next days work.

- Any and all wire, cables (CAT V or VI, telephone, data, etc.) that penetrated non-rated or rated wall, floor or ceiling will be placed in a sleeve and sealed with the proper fire stop materials and systems. After the fire stop has dried and sealed the wire(s) should not be able to move.

- When work is complete and accepted, the permit is removed from the ladder by the Plant Operations Department representative and filed in Plant Operations department.

- No materials, tools, ladders, etc. shall be left unattended in public areas at any time without prior authorization from Plant Operations.

- All wiring, (cables, CAT V or VI, telephone, date etc.) are to be suspended in the proper hangers. They are NOT to be hung or tied in any form or fashion to piping, ducting, ceiling hanger, pipe hanger, etc. or laid directly on top of ceilings or grids.

- No wires, cables or other objects may rest on or be suspended by any fire protection sprinkler piping or supports.

- All, piping, ducting, piping hangers, duct hangers etc are to be suspended in accordance with the latest codes and standards.

- All miscellaneous materials (trash, wall pieces, etc.) are to be removed from above the ceiling.

- All penetrations will be completed in accordance with UL System for Wall Penetrations.

- Facility Representative will conduct a prior to work ceiling tile inspection and count the number of damage or broken ceiling tiles. Upon the completion of the above ceiling work and reinstall of ceiling tiles another inspection will be conducted to record any new ceiling tile damage. Contractor will replace broken ceiling tiles at his expense unless otherwise stipulated in the work agreement.

ABOVE CEILING WORK PERMIT DATE: CONTRACTOR: NAME: ADDRESS: PHONE: CONTACT PERSON: PERSON APPLYING FOR PERMIT: LOCATION OF WORK : Department: Room: Corridor: WILL FIRE OR SMOKE WALLS BE PENETRATED? Yes __________ No __________ TYPE OF WORK: Electrical Data Telephone Other Cables Medical Gases Piping Air Conditioning Seismic Insulation work Lighting Fire systems Nurse call Tube systems Plumbing systems Sewer systems Fire Stopping Project time period: FROM: _____________________ TO: _______________________ WALL PENETRATIONS WILL AFFECT THE FOLLOWING: Rated Fire Walls Non-rated Smoke Walls NUMBER OF ANTICIPATED PENETRATIONS: Facility Engineering signature on prior inspection________________________________________ Facility Engineering Signature on final inspection________________________________________ ABOVE CEILING PERMIT INSTRUCTIONS AND FOLLOW UP This permit must be present on all ladders on which work above the visible ceiling will be done. Working without a permit will be cause for rejection from the hospital. Contractor supervision will be required to meet with hospital representatives to assure a clear understanding of these requirements before staff from that company will be permitted to work in that facility again. To be a valid permit, the Engineering Signature on prior inspection block must be signed. All facility staff are encouraged to report anyone on a ladder without such a permit to Plant Operations.